## Slide 1: Real-time Corrosion Product Transport Monitoring Using On-line Particle Monitors
Joe Zimmerman
Chemtrac Systems, Inc.
Norcross, GA

## Slide 2: Introduction
The goal of CPT monitoring is to determine:
when corrosion is occurring
where corrosion is occurring
how much corrosion is occurring

## Slide 3: Introduction
The ability to monitor CPT in real-time will
allow for:
System control actions to be taken based on the current corrosion product levels
Measurement of the effects of the adjustments on the corrosion product levels

## Slide 4: Introduction
Overview
Steam Cycle Monitoring
Particle Detection Technology
CPT Particle Monitoring
Conclusions

## Slide 5
Steam Cycle Monitoring

## Slide 6: Steam Cycle Monitoring
Traditional Methods
Soluble
  Grab sample tests
    Metals analysis, various other lab analyses
  On-line analyzers
    Cation conductivity, sodium, silica, pH, etc.
  Composite sampling
    Ion exchange columns, resin-impregnated filter pads

## Slide 7: Steam Cycle Monitoring
Traditional Methods
Insoluble
  Grab sample tests
    Millipore pads, TSS, lab particle analyses
  On-line analyzers
    Turbidity monitors
  Composite sampling
    Corrosion Product Monitor filter pads

## Slide 8: Steam Cycle Monitoring
On-line Particle Analysis
provides real-time indication of insoluble particulate loading
allows for continuous data collection & trending

## Slide 9
Particle Detection Technology

## Slide 10: Particle Detection Technology
Turbidity Monitors utilize a “light scattering” measurement
Particle Counters & Particle Monitors utilize a “light blockage” measurement

## Slide 11: Particle Detection Technology
Turbidity Monitor
Lamp
Photo Detector
0.00 NTU
0.30 NTU
Lens

## Slide 12: Particle Detection Technology
Laser Diode
Or LED
Photo Diode
Water Flow
Particles
Light Beam

## Slide 13: Particle Detection Technology
Particle Counter & Particle Monitor
Detect particles > 2 microns
1 particle/mL sensitivity
<10 PPT detection capability

## Slide 14: Particle Detection Technology
Particle Counter
Reports results in counts/mL for up to 8 size ranges
Allows for size/count distribution profiles

## Slide 15: Particle Detection Technology
Particle Monitor
Single channel device, producing a “relative” measurement called a Particle Index (PI)
The PI will increase with both an increase in particle size and concentration

## Slide 16: Particle Detection Technology
Particle Counter, Particle Monitor, Turbidity Monitor
How Are Particles Detected?

## Slide 17: Particle Detection Technology
Magnetite

## Slide 18: Particle Detection Technology
Hematite

## Slide 19
CPT Particle Monitoring

## Slide 20: CPT Particle Monitoring
Steam Generation Cycle

## Slide 21: CPT Particle Monitoring
Particle Counts During Load Change

## Slide 22: CPT Particle Monitoring
HRSG 1 MW
HRSG 1 MW, HRSG 2 MW
HRSG 1 MW, HRSG 2 MW, Particle Index

## Slide 23: CPT Particle Monitoring
Condensate
Condensate pH,
Condensate pH, Cation Conductivity,
Condensate pH, Cation Conductivity & Particles

## Slide 24: CPT Particle Monitoring
Condensate DO,
Condensate DO, ORP
Condensate DO, ORP, & Particles

## Slide 25: CPT Particle Monitoring
Nuclear Plant – Iron Transport Data

## Slide 26: CPT Particle Monitoring
Fossil Plant – CPM Iron vs. Particle Index Average

## Slide 27: CPT Particle Monitoring
Fossil Plant – CPM Iron vs. Particle Index Average

## Slide 28: CPT Particle Monitoring
Fossil Plant – CPM Iron vs. Particle Index Average

## Slide 29
Conclusions

## Slide 30: Conclusions
On-line Particle Monitoring:
Provides continuous tracking of insoluble metal oxides…a clear advantage over “grab” or “composite” sampling
Complements existing online ionic analyzers, offering additional analytical trends for system performance evaluation
Offers real-time CPT results…treatment program adjustments can be made, and subsequent effects on CPT levels can be measured
Allows for real-time recognition of CPT “events” such that immediate actions can be considered when an event occurs